## Bidder Q&A
FM 812 Landfill Solar RFP
ID # | Date Asked | Date Resolved | Asked By | Current Status | Impact | Document Reference | Subject | Question | Owner Response
1 | 2023-09-07 |  | Josephine Hamilton - EDF Renewables | CLOSED | MEDIUM | Appendix A | Gas Collection Infrastructure | Is Austin Energy able to provide a more detailed Alta file, ideally in CAD (.dwg, .shp, or .kmz) format to better inform the design? This will substantially increase the accuracy of the bids. | Drawing of the surface area map and the gas collection infrastructure is provided in this update
2 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Can you please provide any CAD files showing the existing site conditions? | Is provided in this update
3 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Permitting | What is the current status of project permitting, and what permits would the EPC be responsible for? | The permitting process has not started. Per the RFP, Austin Energy (AE) is seeking experienced bidders for the development and EPC of this project. The Bidder will be responsible for all the required permitting
4 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Sitework - General | What do the "Historic Borings" shown on Appendix A represent? | Those are Soil/waste borings drilled in the 1980s during site investigations. They have been plugged and can be ignored
5 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Engineering (Layout, NEC code etc) | The RFP specified 15' setback around all surface gas infrastructure, such as vents, wells, probes, etc. What setbacks should we hold from the condensate sump, the "historic borings", the groundwater monitoring wells, the leachate extraction wells, the leachate collection riser, the downchutes, and any sanitary sewer manholes? | 15-feet. “historic Borings” have been plugged and can be ignored
6 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Please confirm who will be responsible for reflying the site for updated topography (topography shown on the plan is public LIDAR) - Austin Energy or EPC? | EPC
7 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Are there any other site features we need to be made aware of? Appendix A indicated "For Clarity, Not All Site Features Are Shown" | No
8 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Please confirm if there have been any geotechnical studies been performed as a part of this project? If not, would the EPC be responsible for any studies? | No. Bidder would be responsible for all studies including geotechnical
9 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Sitework - General | The RFP stated that the EPC would be responsible for access roads. What constraints must we follow for the location and design of the access roads? | Access road constraints are not available at this time and AE will work with the developer/EPC and provide input during the design of the project
10 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Racking & Foundations | Would Austin Energy entertain the use of ballasted single-axis-tracker in-lieu of ballasted fixed-tilt? | Yes
11 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Sitework-Site improvements | Would we be required to include the use of ballasted fence around the individual array areas? Or would the EPC be responsible for other fence work onsite? | Fencing around the array areas and critical BOS infrastructure is required
12 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Engineering (Layout, NEC code etc) | Does Austin Energy have an idea for where the POI may be located? | POI is yet to be determined and details will be available at a later date after further analysis from AE T&D
13 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Sitework-Erosion, Sediment & Stormwater Controls | What setbacks should we hold to the centerline of the swales on the landfills? | 15 feet
14 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Sitework - General | Are there any ground pressure requirements that we must abide by during construction? | The use of low ground pressure equipment
15 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Engineering (Layout, NEC code etc) | Are there any property line setbacks that we need to be aware of? | 10 ft. on the side if adjacent to another property and 10ft. at the rear of the property, 0 ft. if adjacent to a road, except adjacent to FM973, where there is a waterline easement that extends approximately 60 feet from the property boundary (estimated from Amanda map.)
16 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Engineering (Layout, NEC code etc) | Does the client have any requests for where the pads need to be located, or are we free to locate them as we see fit? | Bidder are free to locate pads as they see fit, as long as they meet the setback requirements and do not interfere with gas collection infrastructure
17 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | How tall is the Flare station on site? | 26 ft.
18 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | General | Is there any Phase 1 or Phase 2 ESA report? | No
19 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Interconnection | Is there any interconnection study already done for this project? If yes, can you provide it? | No
20 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Is there any Approved vendor list available for the equipment selection? | No
21 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Interconnection | Do you have any preference between pole top equipment or switchgear for your interconnection standards? | Interconnections greater than 800A may require switchgear, most common 4kV-34kV distribution circuit breakers are rated up to 2500A
22 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Is the EPC responsible for all equipment selection (from modules to interconnection)? | Yes. Bidder and EPC are responsible for all equipment selection. Austin Energy may provide some input on interconnection and other equipment as the project develops
23 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Please share your interconnection equipment standards (both Austin Energy and ERCOT) so that we can come up with an accurate single line diagram. | Design Criteria Manual
24 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | General | Do you need a three line diagram as well? | Not for the interconnection review, we typically review one-line diagrams during the interconnection process.
25 | 2023-09-15 |  | CS Energy | CLOSED | LOW |  | Interconnection | Can you share your interconnection studies and standards required by both Austin Energy and ERCOT? | AE Interconnection Guide
26 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | General | Can you share any equipment and project specifications that Austin Energy/ERCOT requires us to follow? | None available at this time
27 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Commissioning/Testing | Can you share any testing standards that we need to follow (Austin Energy/ ERCOT) | None available at this time. The developer will provide best practice testing documentation that abide with industry standard
28 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Sitework - General | Please provide specification for well protection, Inlet protection, etc. | No specification is needed. All work should be conducted in a manner which prevents damage to these site features.
29 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Sitework - General | Please provide load restriction on landfill jobsite. | There are no documented load restrictions. If we have an idea of what loads might be, we can do calculations to determine if they are fine for the cap integrity. We plan to perform load restriction calculations as part of the second phase of this RFP and/or development process
30 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Sitework - General | Please advise the expectation of grounding | To be addressed during the second phase of this RFP and/or development process
31 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Insurance & Bond | Please advise builders risk will be provided by Owner | Builders risk will be provided by EPC
32 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | General | Please advise if the project labor will be required to be either Prevailing wage or Union. | Prevailing wage. Use Davis Bacon Act if prevailing wages labor classification is not available for the job title
33 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Sitework-Site improvements | Please advies if we need fence around the landfill. If yes, Please provide specification | No. Only around the array areas and critical BOS infrastructure
34 | 2023-09-15 |  | CS Energy | OPEN | LOW |  | Modules | Please advise if modules will be provided by Owner | No
35 | 2023-09-15 |  | Ameresco | OPEN |  |  | Interconnection | Can Austin Energy please confirm and document the location for the point of interconnection? | POI is yet to be determined and details will be available at a later date after further analysis from AE T&D
36 | 2023-09-15 |  | Ameresco | OPEN |  |  | Local Regulations | Has Austin Energy had any discussion with the area airport authority and FAA regarding this project? If so, can you please share the results of any discussions? | No. Discussion with the airport and/or local FAA officials regarding the project will be held during development